## Site A
Company Name Company Address
Backup Source: Generator | [10 empty] | Ref. Document: NFPA101, 2013 Edition
EMERGENCY LIGHT INSPECTION AND TESTING REPORT
Test Start Time: |  | Test End Time: |  |  | Test Duration Time: |  |  |  |  | Check Date: |  |  | Due Date:
Sl No. | Area/Floor | Light No./ Qty. | Functional (Pcs.) | Non Functional (Pcs.) | AC Power Disconnected | Backup Power Source (Volt) | Source Output (Volt) | Voltage at Appliance (Volt) | Illumination Lux |  |  | Cleaning | Illumination Satisfactory ? | Remarks
[9 empty] | Location/Aeils No | Required | Found
1 | Garmeant's GF | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-1 | 10
2 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-2 | 10
3 |  | 15 | 15 | 0 | Yes | Generator | 220 Volt |  | Cutting Section | 2.5
4 | Garmeant's 1st Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-1 | 10
5 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-2 | 10
6 |  | 21 | 21 | 0 | Yes | Generator | 220 Volt |  | Finishing & Packing Floor | 2.5
7 | Garmeant's 2nd Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-1 | 10
8 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-2 | 10
9 |  | 22 | 22 | 0 | Yes | Generator | 220 Volt |  | Finishing & Packing Floor | 2.5
10 | Garmeant's 3rd Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-1 | 10
11 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-2 | 10
12 |  | 23 | 23 | 0 | Yes | Generator | 220 Volt |  | Sewing Floor | 2.5
13 | Garmeant's 4th Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-1 | 10
14 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-2 | 10
15 |  | 23 | 23 | 0 | Yes | Generator | 220 Volt |  | Sewing Floor | 2.5
16 | Garmeant's 5th Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-1 | 10
17 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-2 | 10
18 |  | 22 | 22 | 0 | Yes | Generator | 220 Volt |  | Sewing Floor | 2.5
19 | Garmeant's 6th Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-1 | 10
20 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-2 | 10
21 |  | 20 | 20 | 0 | Yes | Generator | 220 Volt |  | Sewing Floor | 2.5
22 | Garment's Top Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-1 | 10
23 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-2 | 10
24 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Others Area | 2.5
25 | Printing Section | 31 | 31 | 0 | Yes | Generator | 220 Volt |  | Printing Floor | 2.5
26 | Colour Kitchen Ground Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-1 | 10
27 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-2 | 10
28 |  | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Colour Kitchen Floor | 2.5
29 | Colour Kitchen 1st Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-1 | 10
30 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-2 | 10
31 |  | 3 | 3 | 0 | Yes | Generator | 220 Volt |  | Colour Mixing Floor | 2.5
32 | Colour Kitchen 2nd Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-1 | 10
33 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-2 | 10
34 |  | 3 | 3 | 0 | Yes | Generator | 220 Volt |  | Merchandising Floor | 2.5
35 | Colour Kitchen 3rd Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-1 | 10
36 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-2 | 10
37 |  | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | MD. Sir Room | 2.5
38 | Colour Kitchen Top Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-1 | 10
39 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-2 | 10
40 | Steel Building Cad Section,Sample Section & Embroidery | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-1 | 10
41 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-2 | 10
42 |  | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Cad Section | 2.5
43 |  | 4 | 4 | 0 | Yes | Generator | 220 Volt |  | Sample Section | 2.5
44 |  | 4 | 4 | 0 | Yes | Generator | 220 Volt |  | Embroidery | 2.5
45 | Steel Building 1st Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-1 | 10
46 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-2 | 10
47 |  | 13 | 13 | 0 | Yes | Generator | 220 Volt |  | Accessories Area | 2.5
48 | Steel Building 2nd Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-1 | 10
49 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-2 | 10
50 |  | 11 | 11 | 0 | Yes | Generator | 220 Volt |  | Accessories Area | 2.5
51 | Steel Building 3rd Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-1 | 10
52 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-2 | 10
53 |  | 11 | 11 | 0 | Yes | Generator | 220 Volt |  | Accessories Area | 2.5
54 | Steel Building 4th Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-1 | 10
55 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-2 | 10
56 |  | 11 | 11 | 0 | Yes | Generator | 220 Volt |  | Accessories Area | 2.5
57 | Steel Building Top Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-1 | 10
58 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-2 | 10
59 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Others Area | 2.5
60 | Utiliti Building Genarator, Transformar & Compressor Room | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-1 | 10
61 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-2 | 10
62 |  | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Genarator Room | 2.5
63 |  | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Transformar Room | 2.5
64 |  | 4 | 4 | 0 | Yes | Generator | 220 Volt |  | Compressor Room | 2.5
65 | Maintenance Building Ground Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-1 | 10
66 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-2 | 10
67 |  | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Maintenance Full Area | 2.5
68 | Maintenance Building 1st Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-1 | 10
69 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-2 | 10
70 |  | 3 | 3 | 0 | Yes | Generator | 220 Volt |  | Office Room | 2.5
71 | Maintenance Building 2nd Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-1 | 10
72 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-2 | 10
73 |  | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Security Dormitory | 2.5
74 | Maintenance Building 3rd Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-1 | 10
75 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-2 | 10
76 |  | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Security Dormitory | 2.5
77 | Maintenance Building Top Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-1 | 10
78 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-2 | 10
79 |  | 0 | 0 | 0 | Yes | Generator | 220 Volt |  | Others Area | 2.5
80 | Fire Pump & Worker Canteen Ground floor & Worker Canteen 1st Floor | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Stair-1 | 10
81 |  | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Stair-2 | 10
82 |  | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Fire Pump | 2.5
83 |  | 8 | 8 | 0 | Yes | Generator | 220 Volt |  | Worker Canteen Ground floor | 2.5
84 |  | 8 | 8 | 0 | Yes | Generator | 220 Volt |  | Worker Canteen 1st Floor | 2.5
85 | Carton Section & Elastic Section | 10 | 10 | 0 | Yes | Generator | 220 Volt |  | Carton Section Full Area | 2.5
86 |  | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Elastic Section | 2.5
87 | Yarn Dyeing Ground floor to 1st,2nd floor & Top Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-1 | 10
88 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-2 | 10
89 |  | 3 | 3 | 0 | Yes | Generator | 220 Volt |  | Yern Dyeing | 2.5
90 |  | 10 | 10 | 0 | Yes | Generator | 220 Volt |  | Sewing Thread | 2.5
91 |  | 0 | 0 | 0 | Yes | Generator | 220 Volt |  | Top Floor Full Area | 2.5
92 | RCC Building GF | 0 | 0 | 0 | Yes | Generator | 220 Volt |  | Stair-1 | 10
93 |  | 0 | 0 | 0 | Yes | Generator | 220 Volt |  | Stair-2 | 10
94 |  | 5 | 5 | 0 | Yes | Generator | 220 Volt |  | Dyeing Finishing | 2.5
95 | RCC Building 1st Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-1 | 10
96 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-2 | 10
97 |  | 13 | 13 | 0 | Yes | Generator | 220 Volt |  | OfficeArea & Grey Store | 2.5
98 | RCC Building 2nd Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-1 | 10
99 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-2 | 10
100 |  | 0 | 0 | 0 | Yes | Generator | 220 Volt |  | Lab Section | 2.5
101 | RCC Building 3rd Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-1 | 10
102 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-2 | 10
103 |  | 13 | 13 | 0 | Yes | Generator | 220 Volt |  | Lebtober Area | 2.5
104 | RCC Building 4th Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-1 | 10
105 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-2 | 10
106 |  | 12 | 12 | 0 | Yes | Generator | 220 Volt |  | Cutting Section | 2.5
107 | RCC Building 5th Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-1 | 10
108 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-2 | 10
109 |  | 11 | 11 | 0 | Yes | Generator | 220 Volt |  | Material Store | 2.5
110 | RCC Building 6th Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-1 | 10
111 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-2 | 10
112 |  | 11 | 11 | 0 | Yes | Generator | 220 Volt |  | Finish Fabrics | 2.5
113 | RCC Building Top Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-1 | 10
114 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-2 | 10
115 |  | 0 | 0 | 0 | Yes | Generator | 220 Volt |  | Others Area | 2.5
116 | Dyeing Section | 27 | 27 | 0 | Yes | Generator | 220 Volt |  | Dyeing Full Area | 2.5
117 | Chemical Store | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Chemical Store | 2.5
118 | Genarator, Boiler,LT Room & Transformer Room | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Stair-1 | 10
119 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Genarator | 2.5
120 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Boiler Room | 2.5
121 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | LT Room | 2.5
122 |  | 0 | 0 | 0 | Yes | Generator | 220 Volt |  | Transformer Room | 2.5
123 | Medical,Fire Control room,Super Shop,Coffe Shop,Security Control Room | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Medical room | 2.5
124 |  | 0 | 0 | 0 | Yes | Generator | 220 Volt |  | Fire Control room | 2.5
125 |  | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Super Shop | 2.5
126 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Coffe Shop | 2.5
127 |  | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Security Control Room | 2.5
Authorized By:
Checked By:
NOTE:
1 | A functional test has been conducted on every required emergency lighting system at 30-day intervals for a minimum of 30 seconds.
2 | An annual test has been conducted on every required battery-powered emergency & exit lighting system for not less than 90 minutes. Equipment shall be fully operational for the duration of the test.
3 | Exit signs shall be visually inspected for operation of the illumination sources at intervals not to exceed 30 days.
4 | AC power supply to each emergency & exit light has been disconnected.
5 | Battery backup, output voltage and line checked.
6 | Each emergency & exit light and lens has been cleaned if required.
7 | Beam has been adjusted for proper alignment if required.
8 | Testing label on emergency & exit light and testing log has been placed on the Log Book.
9 | A minimum illumination level (By Emergency Light) of 10lux for all corridors, exit doors and stairways has been checked properly. Aisles shall be provided with a minimum illumination level of 2.5 lux.
As per NFPA standard No. 101-31-1.3.7, A functional test shall be conducted on every required emergency lighting system at 30-day intervals for a minimum of 30 seconds. An annual test shall be conducted for the 1 1/2 hour duration. Equipment shall be fully operational for the duration of the test. Written records of visual inspections and tests shall be kept by the owner for inspection by the authority having jurisdiction.

## Site B
Company Name Company Address
Backup Source: Generator | [10 empty] | Ref. Document: NFPA101, 2013 Edition
EMERGENCY LIGHT INSPECTION AND TESTING REPORT
Test Start Time: |  | Test End Time: |  |  | Test Duration Time: |  |  |  |  | Check Date: |  |  | Due Date:
Sl No. | Area/Floor | Light No./ Qty. | Functional (Pcs.) | Non Functional (Pcs.) | AC Power Disconnected | Backup Power Source (Volt) | Source Output (Volt) | Voltage at Appliance (Volt) | Illumination Lux |  |  | Cleaning | Illumination Satisfactory ? | Remarks
[9 empty] | Location/Aeils No | Required | Found
1 | Garmeant's GF | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Garment's Stair-1 | 10
2 |  | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Garment's Stair-2 | 10
3 |  | 3 | 3 | 0 | Yes | Generator | 220 Volt |  | Garment's Stair-3 | 10
4 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Garment's Emargency Stair | 10
5 |  | 28 | 28 | 0 | Yes | Generator | 220 Volt |  | Knitting & Full Area | 2.5
6 | Garmeant's 1st Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Garment's Stair-1 | 10
7 |  | 4 | 4 | 0 | Yes | Generator | 220 Volt |  | Garment's Stair-2 | 10
8 |  | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Garment's Stair-3 | 10
9 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Garment's Emargency Stair | 10
10 |  | 53 | 53 | 0 | Yes | Generator | 220 Volt |  | Sewing,Finishing & Packing Floor | 2.5
11 | Garmeant's 2nd Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Garment's Stair-1 | 10
12 |  | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Garment's Stair-2 | 10
13 |  | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Garment's Stair-3 | 10
14 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Garment's Emargency Stair | 10
15 |  | 82 | 82 | 0 | Yes | Generator | 220 Volt |  | Sewing,Finishing & Packing Floor | 2.5
16 | Garmeant's 3rd Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Garment's Stair-1 | 10
17 |  | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Garment's Stair-2 | 10
18 |  | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Garment's Stair-3 | 10
19 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Garment's Emargency Stair | 10
20 |  | 86 | 86 | 0 | Yes | Generator | 220 Volt |  | Sewing,Finishing & Packing Floor | 2.5
21 | Garmeant's 4th Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Garment's Stair-1 | 10
22 |  | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Garment's Stair-2 | 10
23 |  | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Garment's Stair-3 | 10
24 |  | 63 | 63 | 0 | Yes | Generator | 220 Volt |  | Garment's Sewing,Finishing & Packing Floor | 2.5
25 | Garmeant's 5th Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Garment's Stair-1 | 10
26 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Garment's Stair-2 | 10
27 |  | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Garment's Stair-3 | 10
28 |  | 58 | 58 | 0 | Yes | Generator | 220 Volt |  | Garment's Cutting Floor | 2.5
29 | Garment's Top Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Garment's Stair-1 | 10
30 |  | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Garment's Stair-2 | 10
31 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Garment's Stair-3 | 10
32 |  | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Garment's Top Floor | 2.5
33 | Admin, Account's & Madical | 3 | 3 | 0 | Yes | Generator | 220 Volt |  | Admin | 2.5
34 |  | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Account's | 2.5
35 |  | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Madical | 2.5
36 | AOP Section | 50 | 50 | 0 | Yes | Generator | 220 Volt |  | AOP Full Area | 2.5
37 | Batch Section & Finish Goods Store | 16 | 16 | 0 | Yes | Generator | 220 Volt |  | Batch Section | 2.5
38 |  | 14 | 14 | 0 | Yes | Generator | 220 Volt |  | Finish Goods Store | 2.5
39 | Fire Pump, Compressore Room, Sub Station Room & ETP | 5 | 5 | 0 | Yes | Generator | 220 Volt |  | Fire Pump | 2.5
40 |  | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Compressore Room | 2.5
41 |  | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Sub Station Room | 2.5
42 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | ETP | 2.5
43 | Dyeing & Dyeing Finishing Section | 13 | 13 | 0 | Yes | Generator | 220 Volt |  | Dyeing Full Area | 2.5
44 |  | 30 | 30 | 0 | Yes | Generator | 220 Volt |  | Dyeing Finishing Full Area | 2.5
45 | LT Room, Generator Room & Boiler Room | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | LT Room | 2.5
46 |  | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Generator Room | 2.5
47 |  | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Boiler Room | 2.5
48 | Washing GF & 1st Floor Section | 12 | 12 | 0 | Yes | Generator | 220 Volt |  | Washing GF Floor | 2.5
49 |  | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Washing 1st Floor | 2.5
50 | Kitchen Room, Staff Canteen & Worker Canteen | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Kitchen Room | 2.5
51 |  | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Staff Canteen | 2.5
52 |  | 8 | 8 | 0 | Yes | Generator | 220 Volt |  | Worker Canteen | 2.5
53 | Brush Room, Wastage Area & Rejection Building | 4 | 4 | 0 | Yes | Generator | 220 Volt |  | Brush Room | 2.5
54 |  | 3 | 3 | 0 | Yes | Generator | 220 Volt |  | Wastage Area | 2.5
55 |  | 8 | 8 | 0 | Yes | Generator | 220 Volt |  | Rejection Building | 2.5
56 | Chamical Store & Bonded Ware House | 22 | 22 | 0 | Yes | Generator | 220 Volt |  | Chamical Store | 2.5
57 |  | 11 | 11 | 0 | Yes | Generator | 220 Volt |  | Bonded Ware House | 2.5
58 | Chest Printing 1st Floor | 3 | 3 | 0 | Yes | Generator | 220 Volt |  | Printing Stair-1 | 10
59 |  | 3 | 3 | 0 | Yes | Generator | 220 Volt |  | Printing Stair-2 | 10
60 |  | 8 | 8 | 0 | Yes | Generator | 220 Volt |  | Printing Production Floor | 2.5
61 | Chest Printing 2nd Floor | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Printing Stair-1 | 10
62 |  | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Printing Stair-2 | 10
63 |  | 14 | 14 | 0 | Yes | Generator | 220 Volt |  | Printing Production Floor | 2.5
64 | Chest Printing 3rd Floor | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Printing Stair-1 | 10
65 |  | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Printing Stair-2 | 10
66 |  | 7 | 7 | 0 | Yes | Generator | 220 Volt |  | Printing Production Floor | 2.5
67 | Chest Printing 4th Floor | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Printing Stair-1 | 10
68 |  | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Printing Stair-2 | 10
69 |  | 14 | 14 | 0 | Yes | Generator | 220 Volt |  | Printing Production Floor | 2.5
70 | Chest Printing 5th Floor | 2 | 2 | 0 | Yes | Generator | 220 Volt |  | Printing Stair-1 | 10
71 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Printing Stair-2 | 10
72 |  | 21 | 21 | 0 | Yes | Generator | 220 Volt |  | Printing Production Floor | 2.5
73 | Chest Printing 6th Floor | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Printing Stair-1 | 10
74 |  | 1 | 1 | 0 | Yes | Generator | 220 Volt |  | Printing Stair-2 | 10
75 |  | 7 | 7 | 0 | Yes | Generator | 220 Volt |  | Printing Production Floor | 2.5
Authorized By:
Checked By:
NOTE:
1 | A functional test has been conducted on every required emergency lighting system at 30-day intervals for a minimum of 30 seconds.
2 | An annual test has been conducted on every required battery-powered emergency & exit lighting system for not less than 90 minutes. Equipment shall be fully operational for the duration of the test.
3 | Exit signs shall be visually inspected for operation of the illumination sources at intervals not to exceed 30 days.
4 | AC power supply to each emergency & exit light has been disconnected.
5 | Battery backup, output voltage and line checked.
6 | Each emergency & exit light and lens has been cleaned if required.
7 | Beam has been adjusted for proper alignment if required.
8 | Testing label on emergency & exit light and testing log has been placed on the Log Book.
9 | A minimum illumination level (By Emergency Light) of 10lux for all corridors, exit doors and stairways has been checked properly. Aisles shall be provided with a minimum illumination level of 2.5 lux.
As per NFPA standard No. 101-31-1.3.7, A functional test shall be conducted on every required emergency lighting system at 30-day intervals for a minimum of 30 seconds. An annual test shall be conducted for the 1 1/2 hour duration. Equipment shall be fully operational for the duration of the test. Written records of visual inspections and tests shall be kept by the owner for inspection by the authority having jurisdiction.