## Master Sheet
Nirapon 90 Days Upload Information
Last Update:7-10-2025
Folder NO | Folder Name | Subject | Time Period | Site B | Site A | Responsible Person
1.1 | Hazard Identification and Risk Assessment | Hazard Identification & risk assessment ,Comitment of HIRA,Hira Committee | after every 3 months | 5-1-2025 next 5-4-2025 |  | Staff 1,Staff 2
1.2 | Comprehensive Safety Policies depending on identified Hazard & associated Risk | Chemical Management Policy | Yearly & as per reveiew |  |  | Staff 1,Staff 2
|  | Communication Management Policy |  |  |  | Staff 1,Staff 2
|  | External Contractors Policy |  |  |  | Staff 1,Staff 2
|  | HIRA Policy |  |  |  | Staff 1,Staff 2
|  | Housekeeping Policy & Procedure |  |  |  | Staff 1,Staff 2
|  | Injury Investigation Policy |  |  |  | Staff 1,Staff 2
|  | Load Management Policy |  |  |  | Staff 1,Staff 2
|  | OHS Policy |  |  |  | Staff 1,Staff 2
|  | Policy for Building and Maintenance |  |  |  | Staff 1,Staff 2
|  | Policy of helpline call |  |  |  | Staff 1,Staff 2
|  | Safe Evacuation Plan & Emergency Response |  |  |  | Staff 1,Staff 2
|  | Hot Work Policy |  |  |  | Staff 1,Staff 2
1.3 | Implementation of factory's Comprehensive Safety Policies | Chemical Management Policy implementation(Picture of Policy Posted on Policy Board, PA Announcement,) | Monthly |  |  | Staff 1,Staff 2
|  | Communication Management Policy implementation (Picture of Policy Posted on Policy Board, Communication Chanel, PA Announcement,) | Monthly |  |  | Staff 8
|  | External Contractors Policy implementation (Picture of Policy Posted on Policy Board, PA Announcement,) | Monthly |  |  | Staff 8
|  | HIRA Policy implementation (Picture of Policy Posted on Policy Board, PA Announcement,) | Monthly |  |  | Staff 8
|  | Housekeeping Policy & Procedure implementation(Picture of Policy Posted on Policy Board, PA Announcement,) | Monthly |  |  | Staff 7
|  | Injury Investigation Policy implementation (Picture of Policy Posted on Policy Board, PA Annaouncement,post injury training, Sickness and Injury analysis report, accident register) | Monthly |  |  | Medical Team
|  | Load Management Policy implementation(Picture of Policy Posted on Policy Board, PA Announcement,) | Monthly |  |  | Staff 1,Staff 2
|  | OHS Policy implementation (Picture of Policy Posted on Policy Board,Training,Pa Announcement, Picture of Various Safety Sign, etc.) | Monthly |  |  | Staff 7
|  | Policy for Building and system Mint. implementation(Picture of Policy Posted on Policy Board, PA Announcement,) | Monthly |  |  | Staff 1,Staff 2
|  | Amader Kotha Policy implementation(Picture of Policy Posted on Policy Board, PA Annaouncement,test call Register, PA Announcement Register, Poster Picture and Other relevant evidence) | Monthly |  |  | Staff 5
|  | Safe Evacuation Plan & Emergency Response implementation(Picture of Policy Posted on Policy Board, PA Annaouncement,Evacuation Plan Picture etc.) | Monthly |  |  | Staff 5
|  | Hot Work Policy implementation(Picture of Policy Posted on Policy Board,Hot Work Permission Announcement,) | Monthly |  |  | Staff 5
2 | Schedule for Safety Management Activities | Annual Training Schedule General | Yearly |  |  | Staff 1,Staff 2
|  | Annual maintenance Schedule(Building) |  |  |  | Staff 1,Staff 2
|  | Annual maintenance Schedule(Electrical) |  |  |  | Staff 4,Staff 3
|  | Annual maintenance Schedule(Fire) |  |  |  | Staff 5
|  | Annual Training Schedule (BRAC) |  |  |  | Staff 1,Staff 2
|  | Brac Training(safety committee, fire safety, fire safety for security guard) | Monthly |  |  | All Brac Trainer
|  | Amader Kotha Policy(Picture of Policy Posted on Policy Board,Training,Pa Announcement,, ,test call Register, PA Announcement Register, Poster Picture and Other relevant evidence) | Monthly |  |  | Staff 5
|  | Chemical Safety Training | Monthly |  |  | Staff 6/Staff 11
|  | Electrical Safety Training | Monthly |  |  | Staff 4,Staff 3
|  | Boiler Safety Training | Monthly |  |  | Staff 4,Staff 3
|  | Fire Drill | Monthly |  |  | Staff 5
|  | Safety Committee Activities(Safety Committee Meeting,Training,Hira Checklist & Report) | Monthly |  |  | Staff 9
|  | Safety Policies Communication(Picture of Policy Posted on Policy Board, PA Announcement, Picture of Various Safety Sign) | Monthly |  |  | Staff 7
3 | Communication of safety policies and implementation of other safety trainings | Amader Kotha Policy(Picture of Policy Posted on Policy Board,Training,Pa Announcement,, ,test call Register, PA Announcement Register, Poster Picture and Other relevant evidence) | Monthly |  |  | Staff 5
|  | Brac Training(safety committee, fire safety, fire safety for security guard) | Monthly |  |  | All Brac Trainer
|  | Safety Committee Activities(Safety Committee Meeting,Training,Hira Checklist & Report) | Monthly |  |  | Staff 9,Staff 7
|  | OHS Policies Communication(Picture of Policy Posted on Policy Board,Training of SOP ,Pa Announcement, Picture of Various Safety Sign) | Monthly |  |  | Staff 7
|  | Boiler Safety Training | Monthly |  |  | Staff 4
|  | Electrical Safety Training | Monthly |  |  | Staff 3
|  | Chemical management Training | Monthly |  |  | Staff 6
|  | Fire Drill | Monthly |  |  | Staff 5
|  | Hot Work Training | Monthly |  |  | Staff 5
|  | Fire Fighter Refreher Training | Monthly |  |  | Staff 5
4 | The Management of Hazardous Materials | Chemical Inventory | Monthly |  |  | Staff 6/Staff 11
|  | Chemical Management Policy posted on notice board | Monthly
|  | Chemical Management Training | Monthly
|  | Chemical DS,Picture of Compatibility Chart,Variuous Safety and other Sign,etc | Monthly
|  | Chemical Room Check List | Monthly
|  | chemical storage fire and explosion risk, storage of fuel for generators fire pumps, storage of gas cylinders, storage of raw materials | Monthly
|  | Chemical Room Image | Monthly
|  | Chemical Spill Drill | Two times in a years
5.1 | Maintaining the Means of Egress | Picture of the Means of Egress,checklist | Daily |  |  | Staff 5
5.2 | Maintaining the Factory Fire Separation Engineered Solution | All Parts of Fire Door picture picture like picture of door leaf,lock,closer,panicbar,cordinator,vison panel,smoke seal,magnetic door holder,overall door function | Monthly |  |  | Staff 5
5.3 | Maintenance of Fire Protection Systems | Fire Pump(Weekly) A. Diesel Engine System(picture as per checklist like fuel tank level, tank float switch,soleniod valve operation, water in system,flexiable hoses and connection) B. Lubrication System(picture as per checklist like oil level, lube oil heater) C. Cooling System(picture as per checklist like level.adquate cooling water to hit exchanger, water pump,conditaion of flexible hoses and connection, jacket water heater.Leakeage) D. Exhaust System (picture as per checklist like Drain Condensate Trap) E. Battery System(picture as per checklist like electrolyte level) F. Electrical System(picture as per checklist like general electrical system) Fire Pump(Monthly) A.Electrical System(picture as per checklist (Excercise Isolating switch and Circuite Breaker) B. Battery System(picture as per checklist case interior clean and dry,spesific gravity or state of charge,charger and charge rate,Equalize charge) C. Electrical System(circuite breaker or fuse) | Monthly |  |  | Staff 5
Quarterly
1st week
2nd week
3rd week
4th week
|  |  | yearly | not started yet |  | Staff 5
|  | Standpipe(Weekly) (Picture as per checklist like presure gauge,sealed,cashing relief valve,pressure relief valve) Standpipe(quarterly) (Picture as per checklist like pressure gauge,hose house,main drain,water level tank without supervised water level alarm connected to constantly attended location,water tank exterior,sorroundiing area,fire depertment connection,hose valve) Standpipe(Monthly) (Picture as per checklist like control valve-locked,control valve electrically supervise,water level tank without supervised water level alarm connected to constantly attended location) Standpipe(Semi Annualy) (Picture as per checklist like control valve temper switches) | Monthly |  |  | Staff 5
Quarterly
1st week
2nd week
3rd week
4th week
|  | Sprinkler(Weekly) (Picture as per checklist like sprinkler head,piping,control valve,fire depertment pumper connection) Sprinkler(quarterly) (Picture as per checklist like water flow device,valve supervisory device,supervisory signal device,primimg water,low air pressure alarm,quick opening device,main drains) Sprinkler(monthly) (Picture as per checklist like physical damage of sprinkler head,coorosion or leake of sprinkler piping,post indicator control valve) Sprinkler(semi-annualy) (Picture as per checklist like supervisory switches ,valve temper alarm) | Monthly |  |  | Staff 5
Quarterly
1st week
2nd week
3rd week
4th week
5.4 | Maintenance of Fire Detection System | Fire alarm & Detection System(Weekly) (Picture as per checklist like Fuses,interfaced equipment,lamps & leds,main power supply,control unit trabol signal) Fire alarm & Detection System(Quarterly) (Picture as per checklist like radiant energy fire detector,image smoke & fire detector,supervisory signal device,waterflow device) Fire alarm & Detection System(Monthly) A. Electrical System (Picture as per checklist like isolating switch circuit breaker or fuse) B.Bateries-fire alarm system(Picture as per checklist like corrosion,leakege,voltage,verify marking of the month/year of manufacture,connection tightness) Fire alarm & Detection System(semi-annualy) (Picture as per checklist like in building fire emergency voice/alarm communication,Battries-sealed lead acid,transient suppressors,initiating annunciator,air samplinf module pipe,duct detector,electromachanical relesing device,fire extinguisher system or suppression Systems switch,smoke detector,heat detector,multi detactor,fire extinguisher electronic monitoring device,carbonmonoxide detector,audiable appliance in fire alaram,text notification,visible appliances-genarel & candrala rating,fuses,interface,lamp/leds,mainpower,secondary power,initiating device,notification appliance) | Monthly |  |  | Staff 5
Quarterly
1st week
2nd week
3rd week
4th week
5.5 | Fire Extinguisher Maintenance | Fire Extinguisher(monthly) (Picture as per checklist like location.refil date,next refil date,no blocking by any object,pressure gauge,prove of material inside,hose & nozle free from crack & tear,pin & tamper seal intact,carreing hande,no dent,leaks,rust,on cillender,attached inspection tag in update.) | Monthly |  |  | Staff 5
6.1 | Generator, Generator room and related electrical equipment Maintenance ((e.g. Automatic Transfer Switch (ATS), Change over switch (COS) etc.) | Generator & Generator room(Daily) (Picture as per checklist Housekeeping,Illumination) Generator & Generator room(Weekly) (Picture as per checklist Instruction board for first aid and artificial respiration,Firefighting equipment,Electric danger/caution signage,Fuel System,Lubrication System & Oil level, Cooling System Level,Cooling System Adequate fresh air through radiator,Exhaust System Leakage,Battery System Electrolyte level, Electrical System General inspection,Prime Mover General inspection,Generator Condition,Generator Automation Operation) Generator & Generator room(monthly) (Picture as per checklist Cover on cable trench,Ground fault protection,Frame earthing,neutral grounding,Working clearance around generator,Ventilation,Combined capacity of fuel tank does not exceed 2500L, Cooling System - Fan & Alternator Belt, Battery System - Clean, State of Charge, Charger & Charge Rate, Equilize charge,Prime Mover - Govenor oil & Linkage) | Daily |  |  | Staff 4
Monthly
Weekly-1st week
2nd week
3rd week
4th week
|  |  | Daily | N/A |  | Staff 3
|  |  | Monthly | N/A
|  |  | Weekly-1st week | N/A
|  |  | 2nd week | N/A
|  |  | 3rd week | N/A
|  |  | 4th week | N/A
|  |  | Daily | N/A |  | Staff 3
|  |  | Monthly | N/A
|  |  | Weekly-1st week | N/A
|  |  | 2nd week | N/A
|  |  | 3rd week | N/A
|  |  | 4th week | N/A
6.2 | Inspection & Testing of Transformer, Substation room and related electrical equipment Maintenance | Sub-Station(Daily) (Picture as per checklist Housekeeping,Illumination,Oil Leaks, Means of security) Sub-Station(Weekly) (Picture as per checklist Dust on windings (Dry type), Bushings,Temperature Indicator,Confirmation of not storing combustible materials,Electric danger/caution signage, Instruction board for first aid and artificial respiration) Sub-Station(monthly) (Picture as per checklist Transformer body earthing,Silica gel,Alignment of horn gap arrestor,Breathing oil cup,Electrical connections,Oil Level,Working clearance around transformer,Ventilation, Cable trench) | Daily |  |  | Staff 4,Staff 3
Monthly
Weekly-1st week
2nd week
3rd week
4th week
6.3 | PS, UPS (Used as backup power of machineries, emergency system etc.) Maintenance | UPS(Monthly) (Picture as per checklist Battery - Float voltage, elNOVrolyte,ECE - Supply voltage, panel meter, lamps,Battery Charger - Output, Panel Meter, Panel Lamps, Load - Panel meters) | Monthly |  |  | Staff 4,Staff 3
6.4 | Electrical Distribution Board Maintenance & Circuit Breaker Test | Panel Board(Daily) (Picture as per checklist Rubber mat,Housekeeping) Panel Board(Weekly) (Picture as per checklist Panel door earthing,Meter (ammeter, voltmeter, PFI controller etc.),Non-existence of combustible material) Panel Board(Monthly) (Picture as per checklist Overloading/overheating/signs of burning,Panel identification,Cable identification,Capacity information label,Dead front construction,Lug/cable termination,Safety signage, Multi-looping,Panel concealment,No higher sized circuit breaker,No circuit is drawn without protection,Physical means to prevent installation of extra overcurrent device,Dedicated neutral,1m clearance in front,2.5 m clearance from washing unit/heat source,Accessible height,DB is not stored inside storage,Operable panel door) | Daily |  |  | Staff 4,Staff 3
Monthly
Weekly-1st week
2nd week
3rd week
4th week
6.5 | Annual Inspection and Testing of Switchgear and protective equipment (e.g. ACB,VCB/LBS) | Annual Inspection and Testing of Switchgear and protective equipment conduc by third party(Yearly) | Yearly | 30/6/2025 next 29/6/2026 | 30/6/2025 next 29/6/2026 | Staff 4,Staff 3
6.6 | Lightning Protection System Maintenance | Lightning Protection System Maintenance(Yearly) | Yearly | 10/10/2024 next=10/10/2025 | 10/10/2024 next=10/10/2025 | Staff 4,Staff 3
6.7 | Thermographic scan | Thermographic scan(Every 4 month) | Every 4 month | 4/3/2025 next= 4/7/2025 | 20/2/2025 next=20/6/2025 | Staff 4,Staff 3
6.8 | Insulation Resistance Measurement | Insulation Resistance Measurement(Yearly) | Yearly | 4/12/2024 next= 4/12/2025 | 21/2/2025 next= 21/2/2026 | Staff 4,Staff 3
6.9 | Earth Resistance Measurement | Earth Resistance Measurement(Yearly) | Yearly | 6/10/2024 next= 6/10/2025 | 10/10/2024 next= 10/10/2025 | Staff 4,Staff 3
6.10. | Transformer Oil Test | Transformer Oil Test(Yearly) | Yearly | 23/12/2024 next=23/12/2025 | 16/2/2025 next 16/2/2026 | Staff 4,Staff 3
6.11 | Solar System Maintenance | Not installed yet | Maintenance |  |  | Staff 4,Staff 3
6.12 | Electrical Load Management Program | Electrical Load Management Program(Quarterly) | Quarterly |  | 24-3-2025 next 23-6-2025 | Staff 4,Staff 3
6.13 | General Electrical System Maintenance (e.g., BBT, Light fixtures with cover in storage area etc.) and other electrical equipments (e.g., Machine, Lift, AC etc.) | Electrical System(Daily) (Picture as per checklist Secured electrical connection,Light fixtures with cover in storage area) Electrical System(Weekly) (Picture as per checklist Shed and reflectors are non-flammable) Electrical System(Monthly) (Picture as per checklist Metal earthing,Junction box cover, Free access for operation and maintenance of cable shaft, Light and socket segregation,Overhead service connection are achieved with covered conductor,Proper cable joint,Cable termination,Cable support, Wiring in storage area is properly concealed,Seismic bracing for light fixtures,Shielding or additional insulation for cables near heat source,Signage for required area (such as storage),Emergency circuit identification,BBT (TOB identification), Higher sized CB, Main floor riser TOB in accessible height,Circuit breaker rating is readable,Concealment of BBT system) | Daily |  |  | Staff 4,Staff 3
Monthly
Weekly-1st week
2nd week
3rd week
4th week
|  | Lift Maintanance(monthly) cleaningness of lift & lift room | Monthly |  |  | Staff 4,Staff 3
|  | Lift Calibration | Every Year | 6/1/2025 next 5/1/2026 | 6/1/2025 next 5/1/2026 | Staff 1,Staff 2
7.1 | Factory Floor Load Management program | Picture as per checklist eg: storage area | after every 2 days for other area |  |  | Staff 1,Staff 2
Daily for storage area
7.2 | Dampness and Water Ponding Maintenance | Picture as per checklist eg: drinking water station,toilet area etc | 2 Times in a month |  |  | Staff 1,Staff 2
7.3 | Corrosion Maintenance | Picture as per checklist eg: steal beam,column etc | Monthly |  |  | Staff 1,Staff 2
Staff 1,Staff 2
Staff 1,Staff 2
7.4 | Structural Crack Maintenance | Picture as per checklist eg: beam,column.beam column joint | 2 Times in a month |  |  | Staff 1,Staff 2
Staff 1,Staff 2
7.5 | Non-Structural Crack Maintenance | Picture as per checklist eg: wall,slab,stair etc | 2 Times in a month |  |  | Staff 1,Staff 2
7.6 | Non-Structural Element Anchorage and Structural Bracing Maintenance | Picture as per checklist eg: storage rack achorage,steamline pipe bracing etc | Monthly |  |  | Staff 1,Staff 2
8.1 | Emergency Light and Exit Sign Maintenance | Picture as per checklist eg: Exit & Emergency Light Lux Test | Monthly |  |  | Staff 5
8.2 | Compressed Gas Cylinder and Gas Connection Maintenance | Picture as per checklist eg: gas coonection ,leakage test etc | Monthly |  |  | Staff 3
8.3 | Boiler & Compressor Maintenance | Picture as per checklist | Daily |  |  | Staff 4,Staff 3
Monthly
Weekly-1st week
2nd week
3rd week
4th week
|  | Yearly hydrolytic pressure test for boiler | Yearly | 31-3-2025 next= 31-3-2026 | 12-1-2025 next= 12-1-2026
8.4 | HVAC Maintenance | Picture as per checklist | Monthly |  |  | Staff 4,Staff 3
9 | Technical Changes & Updates | Picture and document as per change | When change of electric,fire, structure |  |  | Staff 4,Staff 3,Staff 5,Staff 10