## Electrical maintenance program
[Company Name]
[Address]
Electrical Maintenance Program - 2025
Generator Maintenance Schedule
Item | Procedure X-Action R-Replace if needed |  |  |  |  | Frequency D-Daily,W-Weekly,M-Monthly,Q-Quarterly,H-Half-yearly, A-Annually | Remarks
| Visual Inspection | Check | Change | Clean | Test
Generator | As per manufacturer recommendation/ NFPA 110 Attached: Generator Maintenance Log 1, Generator Maintenance Log 2, Generator Maintenance Log 3, Generator Maintenance Log 4, Generator Maintenance Schedule 1, Generator Maintenance Schedule 2, Generator Maintenance Schedule 3 |  |  |  |  | As per manufacturer recommendation/ NFPA 110/ NFPA 70B | Need to create the schedule as per reference and manufacturer recommendation
ATS | As per manufacturer recommendation/ NFPA 70B (Annex F) Attached: Typical Automatic Transfer Switch or Change over switch
COS | As per manufacturer recommendation/ NFPA 70B (Annex F) Attached: Typical Automatic Transfer Switch or Change over switch
Generator room related Schedule
Brand: TEMPEST Engine: ****135D, ****370G, ****373G | Procedure X-Action R-Replace if needed |  |  |  |  | Frequency D-Daily,W-Weekly,M-Monthly,Q-Quarterly,H-Half-yearly, A-Annually | Remarks
Item | Visual Inspection | Check | Change | Clean | Test
Instruction board for first aid and artificial respiration | X |  |  |  |  | W
Cover on cable trench | X |  |  |  |  | M
Ground fault protection |  |  | R |  | X | M
Firefighting equipment | X |  |  |  |  | W
Exhaust discharge in a safe location | X |  |  |  |  | H
Electric danger/caution signage | X |  |  |  |  | W
Frame earthing,neutral grounding | X |  |  |  |  | M
Working clearance around generator | X |  |  |  |  | M
Housekeeping |  |  |  | X |  | D
Illumination |  | X |  |  |  | D
Fire rated separation | X |  |  |  |  | A
Ventilation | X |  |  |  |  | M
Combined capacity of fuel tank does not exceed 2500L | X |  |  |  |  | M
Substation Maintenance Schedule
Substation 1 & 2 (Garments & Dyeing) | Procedure X-Action R-Replace if needed |  |  |  |  | Frequency D-Daily,W-Weekly,M-Monthly,Q-Quarterly,H-Half-yearly, A-Annually | Remarks
Item | Visual Inspection | Check | Change | Clean | Test
Transformer | As per NFPA 70B (Annex F) Attached: Transformer test and inspection report |  |  |  |  | A | Need to create the schedule as per reference and manufacturer recommendation
PFI | As per manufacturer recommendation |  |  |  |  | As per manufacturer recommendation
Substation room related Schedule
Item | Procedure X-Action R-Replace if needed |  |  |  |  | Frequency D-Daily,W-Weekly,M-Monthly,Q-Quarterly,H-Half-yearly, A-Annually | Remarks
| Visual Inspection | Check | Change | Clean | Test
Transformer body earthing | X |  |  |  |  | M
Silica gel | X |  |  |  |  | M
Alignment of horn gap arrestor | X |  |  |  |  | M
Breathing oil cup | X |  |  |  |  | M
Dust on windings (Dry type) | X |  |  |  |  | W
Electrical connections |  | X |  |  |  | M
Bushings |  |  |  | X |  | W
Oil Level | X |  |  |  |  | M
Oil Leaks | X |  |  |  |  | D
Temperature Indicator | X |  |  |  |  | W
Arrangements exist to prevent the entrance of storm or flood water into the substation area | X |  |  |  |  | Q
Soak pit | X |  |  |  |  | A
Working clearance around transformer | X |  |  |  |  | M
Fire rated separation | X |  |  |  |  | A
Ventilation | X |  |  |  |  | M
Illumination |  | X |  |  |  | D
Confirmation of not storing combustible materials | X |  |  |  |  | W
Electric danger/caution signage | X |  |  |  |  | W
Instruction board for first aid and artificial respiration | X |  |  |  |  | W
Housekeeping |  |  |  | X |  | D
Confirmation of not routing foreign utilities through room | X |  |  |  |  | H
Means of security | X |  |  |  |  | D
Cable trench | X |  |  |  |  | M
IPS/UPS Maintenance Schedule
Item | Procedure X-Action R-Replace if needed |  |  |  |  | Frequency D-Daily,W-Weekly,M-Monthly,Q-Quarterly,H-Half-yearly, A-Annually | Remarks
| Visual Inspection | Check | Change | Clean | Test
IPS | As per NFPA 110, Ed 2005, Ch-8, (Table A.8.3.2) Attached: IPS UPS maintenance checklist, IPS UPS maintenance schedule 1, IPS UPS maintenance schedule 2 |  |  |  |  | As per reference | Need to create the schedule as per reference
UPS | As per NFPA 70B (Annex F) Attached: UPS inspection checklist |  |  |  |  | As per reference
Boiler Maintenance Schedule
Boiler 1 & 2 (10 Bar & 18 Bar) | Procedure X-Action R-Replace if needed |  |  |  |  | Frequency D-Daily,W-Weekly,M-Monthly,Q-Quarterly,H-Half-yearly, A-Annually | Remarks
Item | Visual Inspection | Check | Change | Clean | Test
Boiler maintenance log sheet |  | X |  |  |  | D
Precaution measures taken before entering any boiler room/ Access restriction for unauthorized person to entry in boiler room | X |  |  |  |  | D
Arrangement of smoke removing or arrangement of ventilation system | X |  |  |  |  | D
Visual inspection of Boiler (Check burner flame, check boiler and system for leaks, boiler room/surrounding cleanness, temperature readings, water level indicators, unobstructed or free of materials, any error codes or service codes on the display panel, pressure gauge etc ) | X |  |  |  |  | D
Precaution of fire incident and steam increasing / Emergency precaution in emergency basis | X |  |  |  |  | D
Supplying pure water, cleanness and protection of spot of heat surface or other surface. | X |  |  |  |  | D
Checking water crisis in boiler or steam pipe, swelling, chimney condition, falling of sheets or bursting of pipe including other incidents | X |  |  |  |  | D
Hazards of storing water in steam pipe and precaution for water discharge | X |  |  |  |  | D
Boiler electrical control panel |  | X |  |  |  | M
Emergency shutdown buttons at exits |  | X |  |  |  | M
Pressure of safety valve. |  | X |  |  |  | M
Perfectness of water measuring glass. |  | X |  |  |  | M
Pump or valve glands locking |  | X |  |  |  | M
Separation and connection of cocks and valve |  | X |  |  |  | M
Low water level cutoff switch |  | X |  |  |  | M
Bottom blow down |  | X |  |  |  | M
Smoke prevention method / Checking fire alarm system in boiler room |  | X |  |  |  | M
Unused boiler maintenance | X |  |  |  |  | M
Certification of boiler operator | X |  |  |  |  | A
Certification of boiler | X |  |  |  |  | A
Water softener |  | X |  |  |  | A
Heating surface |  | X |  |  |  | A
Firing system (flame sensors, ignitor, and burner assembly) |  | X |  |  |  | A
Water pH levels |  |  |  |  | X | A
Venting system for deterioration, corrosion, or blockage to ensure all pipe and joint connections are secure |  | X |  |  |  | A
Control settings as well as test safety controls and operating controls |  |  |  |  | X | A
Super heater, economizer, feed heater and required machineries. |  | X |  |  |  | A
Hydrostatic pressure test |  |  |  |  | X | A
Efficiency of Boiler |  |  |  |  | X | A
Feed water pump |  | X |  |  |  | A
Various valve, cocks, mounting and fitting |  | X |  |  |  | A
Connection of manhole or hand hole or any cover or any ends of steam or feed pipe |  | X |  |  |  | A
Renewing or replace low water cut-off switch and fuse able plug |  |  | R |  |  | A
Compressor Maintenance Schedule
Compressor 1, 2 & 3 (55KW, 55KW, 75KW) | Procedure X-Action R-Replace if needed |  |  |  |  | Frequency D-Daily,W-Weekly,M-Monthly,Q-Quarterly,H-Half-yearly, A-Annually | Remarks
Item | Visual Inspection | Check | Change | Clean | Test
Inspect all air leaks | X |  |  |  |  | D
Check and replace air filter and oil filters,if required to manufacturer’s specification. |  | X | R |  |  | W
Check Pump Oil Level |  | X |  |  |  | D
Inspection oil Leak | X |  |  |  |  | D
Check for any unusual noise or vibration. |  | X |  |  |  | D
Drain water in tank | X |  |  |  |  | D
Regularly check the condition and tension of drive belts where fitted |  | X |  |  |  | W
check safety relief valve |  | X |  |  |  | M
Check and tighten all bolts |  | X |  |  |  | M
Check service pump or engine |  | X |  |  |  | A
Check operating temperatures and pressures. |  | X |  |  |  | D
Visual check of mains electrical switches, wiring and/or conduit (cracks, broken controls etc.) Arrange for immediate repair of any faults. | X |  |  |  |  | W
Clear away all dust, fines, grit, and waste from inside and around housings, cabinets etc. | X |  |  |  |  | D
All guards around moving parts in place | X |  |  |  |  | W
Compressor in safe working condition | X |  |  |  |  | W
Conduct any checks as required to the manufacture specifications. |  | X |  |  |  | D
Log book available and in use |  | X |  |  |  | W
Service and lubricate the compressor as per the manufacturer’s specification. | X |  |  |  |  | W
Be sure to inspect the motor bearings | X |  |  |  |  | Q
Check all control valves for proper operation. |  | X |  |  |  | A
Check all safety devices for proper settings and operation |  | X |  |  |  | A
Check control panel for complete and proper operation. |  | X |  |  |  | A
Check safety shutdown system. |  | X |  |  |  | A
Check drive motor amps at compressor full capacity and design pressure. |  | X |  |  |  | M
Perform valve inspection per manufacturer’s manual. | X |  |  |  |  | Q
Inspect cylinder or cylinder liner, through valve port, for scoring. | X |  |  |  |  | Q
Remove and clean crankcase lubricant strainer. |  |  | R |  |  | A
Panel board Maintenance Schedule
Item | Procedure X-Action R-Replace if needed |  |  |  |  | Frequency D-Daily,W-Weekly,M-Monthly,Q-Quarterly,H-Half-yearly, A-Annually | Remarks
| Visual Inspection | Check | Change | Clean | Test
Electrical Panel Board | As per NFPA 70B (Annex F) Attached: Typical PanelboardCircuit Breaker Test Report |  |  |  |  | A | Need to create the schedule as per reference
Panel board related Schedule
Item | Procedure X-Action R-Replace if needed |  |  |  |  | Frequency D-Daily,W-Weekly,M-Monthly,Q-Quarterly,H-Half-yearly, A-Annually | Remarks
| Visual Inspection | Check | Change | Clean | Test
Panel door earthing |  |  |  |  | X | W
Rubber mat | X |  |  |  |  | D
Meter (ammeter /voltmeter/PFI controller etc.) |  | X |  |  |  | W
Housekeeping |  |  |  | X |  | D
Non-existence of combustible material | X |  |  |  |  | W
Overloading/overheating/signs of burning |  |  |  |  | X | M
Panel identification | X |  |  |  |  | M
Cable identification |  | X |  |  |  | M
Capacity information label |  | X |  |  |  | M
Dead front construction | X |  |  |  |  | M
Lug/cable termination |  | X |  |  |  | M
Safety signage | X |  |  |  |  | M
Multi-looping | X |  |  |  |  | M
Phase separator | X |  |  |  |  | W
Ingress of water | X |  |  |  |  | W
Panel concealment | X |  |  |  |  | M
No higher sized circuit breaker |  | X |  |  |  | M
No circuit is drawn without protection |  | X |  |  |  | M
Physical means to prevent installation of extra overcurrent device | X |  |  |  |  | M
Dedicated neutral |  | X |  |  |  | M
1m clearance in front | X |  |  |  |  | M
2.5 m clearance from washing unit/heat source | X |  |  |  |  | M
Accessible height | X |  |  |  |  | M
DB is not stored inside storage | X |  |  |  |  | M
Operable panel door |  | X |  |  |  | M
Electrical Switchgear maintenance Schedule
Item | Procedure X-Action R-Replace if needed |  |  |  |  | Frequency D-Daily,W-Weekly,M-Monthly,Q-Quarterly,H-Half-yearly, A-Annually | Remarks
| Visual Inspection | Check | Change | Clean | Test
ACB | As per NFPA 70B (Annex F) Attached: ACB test and inspection report |  |  |  |  | A
VCB | As per NFPA 70B (Annex F) Attached: VCB inspection and test report |  |  |  |  | A
OCB | As per NFPA 70B (Annex F) Attached: OCB test report |  |  |  |  | A
Disconnecting Switch/ LBS | As per NFPA 70B (Annex F) Attached: Disconnect switch test report |  |  |  |  | A
LPS maintenance Schedule
Item | Procedure X-Action R-Replace if needed |  |  |  |  | Frequency D-Daily,W-Weekly,M-Monthly,Q-Quarterly,H-Half-yearly, A-Annually | Remarks
| Visual Inspection | Check | Change | Clean | Test
The system is in good repair /Inspection of all conductors and system components. |  | X |  |  |  | A
There are no loose connections that might result in high-resistance joints/Tightening of all clamps and splicers. |  | X |  |  |  | A
No part of the system has been weakened by corrosion or vibration. | X |  |  |  |  | A
All down conductors and grounding electrodes are intact/Ground rod is easily accessible for maintenance |  | X |  |  |  | A
All conductors and system components are fastened securely to their mounting surfaces and are protected against accidental mechanical displacement as required/Refastening and tightening of components and conductors as required. |  | X |  |  |  | A
There have not been additions or alterations to the protected structure that would require additional protection.Inspection and testing as required to determine if the effectiveness of the lightning protection system has been altered by additions to or changes in the structure. | X |  |  |  |  | A
There is no visual indication of damage to surge suppression (overvoltage). | X |  |  |  |  | A
The system complies in all respects with the current edition of this standard.Any variations from the requirements contained in this standard | X |  |  |  |  | A
Measurement of resistance of grounding electrodes |  |  |  |  | X | A
External metal bonding | X |  |  |  |  | A
Need to ensure that lightning protection system is properly installed and maintained following reviewed drawing |  | X |  |  |  | A
Tests to verify continuity of LPS |  |  |  |  | X | A
Electrical System maintenance Schedule
Item | Procedure X-Action R-Replace if needed |  |  |  |  | Frequency D-Daily,W-Weekly,M-Monthly,Q-Quarterly,H-Half-yearly, A-Annually | Remarks
| Visual Inspection | Check | Change | Clean | Test
Metal earthing |  | X |  |  |  | M
Junction box cover | X |  |  |  |  | M
Free access for operation and maintenance of cable shaft | X |  |  |  |  | M
Light and socket segregation |  | X |  |  |  | M
Overhead service connection are achieved with covered conductor | X |  |  |  |  | M
Proper cable joint |  | X |  |  |  | M
Cable termination | X |  |  |  |  | M
Secured electrical connection | X |  |  |  |  | D
Cable support | X |  |  |  |  | M
Light fixtures with cover in storage area |  | X |  |  |  | D
Wiring in storage area is properly concealed |  | X |  |  |  | M
Seismic bracing for light fixtures |  | X |  |  |  | M
Mechanical guard | X |  |  |  |  | M
Separation of power and telecommunication cable |  | X |  |  |  | H
Shielding or additional insulation for cables near heat source |  | X |  |  |  | M
Signage for required area (such as storage) | X |  |  |  |  | M
Underground service cables are encased in GI/PVC pipe and laid in earth trench of sufficient depth |  | X |  |  |  | A
Emergency circuit identification | X |  |  |  |  | M
Ground fault overcurrent protection device for generator |  | X |  |  |  | A
BBT (TOB identification) | X |  |  |  |  | M
Higher sized CB |  | X |  |  |  | M
Main floor riser TOB in accessible height | X |  |  |  |  | M
Circuit breaker rating is readable | X |  |  |  |  | M
Concealment of BBT system | X |  |  |  |  | M
Shed and reflectors are non-flammable | X |  |  |  |  | W
Electrical System Testing Schedule
Item | Procedure X-Action R-Replace if needed |  |  |  |  | Frequency D-Daily,W-Weekly,M-Monthly,Q-Quarterly,T-Triannually, H-Half-yearly, A-Annually | Remarks
| Visual Inspection | Check | Change | Clean | Test
Thermographic Scanning |  |  |  |  | X | T
Insulation Resistance Test |  |  |  |  | X | A
Earth Resistance Test (System) |  |  |  |  | X | A
Earth Resistance Test (LPS) |  |  |  |  | X | A
Transformer oil test |  |  |  |  | X | A
Load measurement |  | X |  |  |  | Q
Electrical Safety Training Schedule
Item | Procedure X-Action R-Replace if needed |  |  |  |  | Frequency D-Daily,W-Weekly,M-Monthly,Q-Quarterly,H-Half-yearly, A-Annually | Remarks
Training
Electrical Safety Training | X |  |  |  |  | H
Prepared By & Checked By | [5 empty] | Approved By HOD (Maintenance)