## General Guidelines
90-Day Management Guidance and Reporting Process V2.15 (31 December 2023)
General Guidelines: Please read this guidance before starting the implementation of the process. Preserve documents, pictures, or videos that reflect the activities performed, along with maintenance and testing reports. Share these activities by uploading them to SharePoint upon completion of the task. This is referred to as 'real-time' reporting, which will ultimately demonstrate the regular implementation of the program. If the pictures or videos are date-stamped, it will be easier to identify when the activities were captured.
The importance of a safety management program in a factory cannot be overstated, as it plays a vital role in maintaining a safe and healthy work environment. At its core, the program aims to protect the well-being of employees by identifying and listing all hazards at the factory. Then a Hazard Identification and Risk Assessment process can be implemented, to reduce risk and control all hazards. This reduces the likelihood of accidents, injuries, and fatalities. A well-implemented safety management program fosters a culture of safety consciousness, where workers are encouraged to actively participate in maintaining a secure workplace. Moreover, such a program ensures compliance with legal and regulatory requirements, helping factories avoid fines, penalties, and reputational damage. Ultimately, a robust safety management program contributes to increased productivity, cost savings, and long-term business success by minimizing disruptions and promoting a stable, secure work environment.
90-Day Safety Monitoring Report Overview The 90-Day Safety Management Guidance and Monitoring Report supports and directs factory managers and owners in understanding the necessary systems and processes for effective factory safety management. Utilizing a systems-based approach, which includes a 12-month schedule for safety management and maintenance events, promotes a culture of prevention, planning, and hazard control, rather than reacting to accidents and major incidents. The attached report guides factory management to create a framework of regular safety management and maintenance events integrated into daily operations based upon the identified hazards and risk along with the preventive maintenance requirements and activities. Bulk loading large amounts of evidence does not indicate that work is being done and is counterproductive. If the evnet is carried out the evidence to support the activity will naturally occur. The 90-Day report consists of three sections. The first two sections instruct factories on maintaining and managing a safe environment. In some cases, specialists like engineers will be required for technical support on topics such as boiler maintenance or electrical load management. Efficient evidence collection and record-keeping, managed by the appointed manager or relevant team, facilitates streamlined reporting. This is not the job of a complaince manager constantly taking photos or gathering documents to support work. The people doing the work can gather the evidence as they carry out the safety function, thus it is then naturally occuring evidence. Section 1 Safety Management provides guidelines to factories on how to develop an annual plan for safety management duties, responsibilities, policies, training and protocol while specifying necessary levels of management oversight of safety. This work will be based upon the hazards and risk identified at the factory, along with the control measures to control those hazards and reduce the risk. Section 2 Safety Maintenance provides guidelines to factories on safety maintenance procedures to sustain all factory production systems, utility suystems and safety engineering solutions within the factory; this will include the interaction of the people in the factory. Safety management and safety maintenance vary from factory to factory. This variance is dependent upon many factors such as the identified hazards and risk, the construction and size of the factory, the production machinery and utility systems in place, such as natural gas, electrical supply, the production processes (such as use of hazardous substances), the number of workers and their individual tasks in the overall production process and any safety engineered solutions in place. This list of variable factors is not exhaustive. However, the potential complexity of different risk profiles demonstrates the importance of the workforce’s ability to identify hazards, and then control, and mitigate risk supported by leadership.
Section 3, Technical Changes & Updates, should only be completed when a factory undergoes significant modifications to the building structure or engineered safety solutions. Adhere to the processes in Section 3 (when applicable) to maintain the building's integrity and CAP closure status. Material changes may include expansions or extensions, adding production lines, or altering the use of floor space. An expansion refers to a structurally independent building, separate from the original CAP-closed structure, but possibly connected by utilities and some engineered safety solutions, such as hydrant systems and central fire detection system electrical supply.
An extension is defined as a vertical or horizontal addition to a building, structurally linked to the original CAP-closed factory. The extended structure shares utilities and engineered safety solutions, such as utilities supply, hydrant system, and CFDS, with the original building. An expansion refers to an additional building linked to the original CAP-closed building by utilities hazards and engineered safety solutions. Section 3 of the report, typically requires consulting engineering firm assistance. Sections 1 and 2 focus on maintaining a safe, well-managed factory, occasionally requiring specialist engineers for tasks such as boiler maintenance or CFDS technical maintenance.
Adopting a self-monitoring approach with photographic, video, and documentary evidence may result in extending frequency of the Safety Support Visit 18 months or 2 years, or where more support is needed it may be reduced to 12 months. By following the attached Safety Management Guidance and Monitoring Report, factories can establish an effective safety management system, providing assurance to members and demonstrate sustainable safety solutions are in place. for the Bangladesh RMG sector. All factories are instructed to utilize a SharePoint site for sharing the activities as part of the safety management program, replacing previous disparate platforms. This change enables factories to submit information continuously, rather than waiting until the end of the 90-Day reporting cycle. In order to make the reporting process easier, folders are created in SharePoint keeping the folder sequence according to the same number arrangement as this excel file. So, following this excel file sequence will reduce the confusion regarding where to upload the relevant activities. Factory can use Columns (Comments from Factory, Response from Factory at safety management, safety maintenance, technical changes & updates tap) to share the information related to availability of any system, equipment and technical changes etc. All work will be reviewed on the assigned review date, with feedback and suggestions for continuous improvement provided to you through a summary level report.

## Safety Management
Factory Name |  |  |  | FFC ID
Factory Address |  |  |  | Number of People**
** If multiple business ID (FFC ID) located in same locale then number of people should be provided as per business ID
Safety Management Policy, and Procedures (Annual Submission or Change in policy)
S.N | Code Provision |  | Benefits and Importance | Guidelines and References | Comments from Factory | Response from Factory
Yes / No / Not Applicable
1 | Comprehensive Safety Policies depending on identified Hazard & associated Risk and adherence to those policies | 1.1 Hazard Identification and Risk Assessment | • Attracting and retaining talent: Factories with strong safety policies are more likely to attract and retain skilled workers who value their well-being. • Enhanced productivity and efficiency: A safe and healthy workplace promotes worker satisfaction and engagement, leading to increased productivity and efficiency. • Improved worker safety and health: Comprehensive safety policies, such as OHS and HIRA, help identify hazards, assess and reduce risks, and implement control measures to prevent accidents and injuries. • Reduced costs: Implementation of safety policies can save factory's money by reducing medical expenses, compensation costs, and lost work time. • Enhanced reputation: Implementing robust safety policies demonstrates a factory's commitment to ethical business practices, which can boost reputation and customer loyalty. Also, demonstrating a commitment to worker safety can strengthen relationships with stakeholders, including investors, employees, and local communities. | https://nirapon.sharepoint.com/:f:/s/NiraponDocumentCenterbd/EnnFjDMw8WhLrZ0wYAWCYqYBpG0uvn4oCyxrgNXkRCqgnA?e=X9qjgT
|  | 1.2 Comprehensive Safety Policies depending on identified Hazard & associated Risk |  | https://nirapon.sharepoint.com/:f:/s/NiraponDocumentCenterbd/Ek9NQQometJDrYuv0L8dN3cBkOJr2Ia5b61AtTAaM6clXA?e=jk9sB8
|  | 1.3 Implementation of factory's Comprehensive Safety Policies |  | https://nirapon.sharepoint.com/:f:/s/NiraponDocumentCenterbd/EqGgdG0PxSZKvVAmPv4NO4QB82S_WhwiXRocxoRBGWm1tA?e=IEjRZi
2 | Schedule for Safety Management Activities | Annual training schedule and other safety management activities (safety policies communication, chemical, boiler & electrical safety trainings, fire drill, helpline implementation, BRAC safety trainings etc.) | • Enhanced safety and productivity: Training and safety management activities improve worker awareness, reduce accidents, and contribute to a more productive and efficient workforce. • Adherence and reputation: These activities help factories to minimize risks, and promote a positive reputation by demonstrating a commitment to ethical business practices. • Continuous improvement and talent retention: A strong safety culture fosters ongoing learning, best practice adoption, and attracts skilled workers, reducing turnover and driving operational excellence. | https://nirapon.sharepoint.com/:f:/s/NiraponDocumentCenterbd/EueFtCEiUSRKgc_Y5jnK-tgBtCD3KEVrlfmVGN3k-QEVWw?e=svhtb1
|  | Annual safety maintenance schedule to cover all preventative maintenance (Structural, electrical, all engineered fire safety elements of the building including Boilers/Generators/Gas supplies and other ancillary equipment) | • Enhanced safety and reliability: An annual safety maintenance schedule assists in maintaining sustainable operations for all equipment and building elements, consequently minimizing the risk of accidents, malfunctions, and downtime. • Improved efficiency and longevity: Regular maintenance optimizes equipment performance, contributing to higher productivity and extending the lifespan of factory assets. • Cost savings and compliance: Preventative maintenance identifies potential issues early, lowering repair costs, and helps factories meet industry standards. Scheduling maintenance also allows for proper budgeting of related maintenance costs. | https://nirapon.sharepoint.com/:f:/s/NiraponDocumentCenterbd/Et3cTcxOQZBHnVxi2VMT6RkBD8TPTJ8rOAUxo9SnO_IR-Q?e=ADPk7B
3 | Communication of safety policies and implementation of other safety trainings | Communication of factory's safety policies | • Culture of safety: Effective communication fosters a strong safety culture, promoting responsibility, accountability, and collaboration among workers. • Awareness and compliance: Communicating safety policies ensures workers understand the protocols and guidelines, leading to better compliance and a safer working environment. • Accident prevention: Clear communication of safety policies helps workers identify hazards and adopt best practices, reducing the likelihood of accidents and injuries. • Enhance awareness: Safety trainings in garment factories enhance safety awareness, reduce accidents, improve emergency response, ensure compliance with regulations, and empower workers, leading to a safer, more efficient work environment and increased employee retention. | https://nirapon.sharepoint.com/:f:/s/NiraponDocumentCenterbd/EnD5T083xpZDsZ4VtjBozzABfIkfoUSO4c0VS7SySB0G0w?e=d2eCHv
Implementation of other safety trainings (chemical, boiler & electrical safety trainings, fire drill, helpline implementation, BRAC safety trainings etc.)
4 | The Management of Hazardous Materials | Comprehensive policy for chemical management and safe management of hazardous materials for storage and use (e.g., chemical storage fire and explosion risk, storage of fuel for generators fire pumps, storage of gas cylinders, storage of raw materials and finished goods etc.) (This list is not exhaustive and managers should assess the risk of all items) | • Optimizing safety and efficiency with chemical management: Implementing a comprehensive policy and communicating it for chemical management and safe handling of hazardous materials in garment factories ensures proper storage and use, minimizes fire and explosion risks, reduces accidents, maintains compliance, and protects workers, equipment, and the environment, ultimately contributing to a safer and more efficient workplace. | https://nirapon.sharepoint.com/:f:/s/NiraponDocumentCenterbd/EikxIkzBH2hMvKnXSdYlaGsBeNykLqa71VXzihymDx6Ezg?e=LjoYhe

## Safety Maintenance
Factory Name |  |  |  | FFC ID
Factory Address |  |  |  | Number of People**
** If multiple business ID (FFC ID) located in same locale then number of people should be provided as per business ID
Code Provision |  |  | Benefits and Importance | Guidelines and References | Comments from Factory | Response from Factory
Yes / No / Not Applicable
Fire Safety Engineering Systems Preventative Maintenance | 5.1 | Maintaining the Means of Egress | • A means of egress is the path of travel from the building to the outside. It is the emergency escape route in case of fire or other emergency and includes the fire exits, stairs, and walkways that allow occupants to exit the building. • A safe evacuation cannot be achieved if there are any obstructions in the means of egress, fire separation is not maintained in exit pathways and locked doors in the exit pathways. This can result in Injury or death, due to for example, such things as stampedes of large panicked crowds or death through smoke inhalation. • Marking (aisles, passageways, exit sign) and inspection/monitor of exit pathways should be taken place with proper training among the factory personnel. • By maintaining means of egress, the factory demonstrates a culture of safety to the worker in addition to the other benefits mentioned. | • BNBC 2006 Part 4 Section 3.9.3, Section 3.9.8, Section 3.10.8 • BNBC 2020 Part 4 Section 3.9.3, Section 3.9.7.5, Section 3.10.11 (applicable for structures according to this standard) • NFPA 101 (Edition 2018) Section 7.1.3, Section 7.1.9; Section 7.1.10, Section 7.2.2.5.2, Section 7.7.2, Section 7.1.5 Section 7.2.1.2.3 • IBC Edition 2018 Section 1028
https://nirapon.sharepoint.com/:f:/s/NiraponDocumentCenterbd/EsBeVf38ULdCp2LqA5sK3TcBSxaInAm45I-sY74-ih-PfA?e=2HJKrg
| 5.2 | Maintaining the Factory Fire Separation Engineered Solution | • Fire Separation provides occupiers of the building additional time to evacuate before escape routes are potentially compromised by the spread of smoke and fire. It will also decrease the danger of fire spread containing the fire to the location where it has originated. • While fire walls and doors, fire rated materials are aspects of fire separation that can significantly reduce the chance of fire spreading, they can be weaknesses too, if not maintained properly. For example, a firewall can have a corroded concrete case, a fire-resistant construction may have deteriorated, or fire doors may be propped open. Other common issues occur when non-rated penetration is available in walls and either haven’t been sealed or have been sealed with combustible or flammable items. Compromise in fire separation can lead the fire spread to an uncontrolled way, allow heat and smoke to pass into the exit pathway etc. which ultimately interrupt safe evacuation, cause injury or death of the occupants. • Fire separation construction materials (such as fire separation construction wall, fire doors, gypsum board, expansion gap sealant, fire damper, fire rated shutter, fire rated lift landing door etc.) should be inspected and maintained on regular basis to ensure the fire separation. Fire separation requirement due to change in occupancy, excessive storage etc. should also be monitored regularly. | • BNBC 2006 Part 3 Table 3.2.1, Table 3.2.3, Table 3.3.1, Part 4 Section 2.5 • BNBC 2020 Part 3 Table 3.2.1, Table 3.2.3, Table 3.3.1a & 3.3.1b, Part 4 Section 2.5 (applicable for structures according to this standard) • NFPA 80 Chapter 5
https://nirapon.sharepoint.com/:f:/s/NiraponDocumentCenterbd/Em04ORTRGvFCmw33edjQRuEB-di16D6jqoKZHEsa-PFFnw?e=tm0GQ4
| 5.3 | Maintenance of Fire Protection Systems | • Fire protection system can be consist of Standpipe, fire pump set and automatic sprinkler system which can be used for extinguishing fire in case of emergency to protect both life and property. Periodic maintenance of fire protection system helps keeping the system active for anytime usage, avoids any malfunction or failure of equipment and increase the life span of the system. | • NFPA 25 Chapter 5, 6 and 8
https://nirapon.sharepoint.com/:f:/s/NiraponDocumentCenterbd/EiW3RNXyV5JFvgIQbwEQu5gBVUpTrWe_Zjpille0lEEU2Q?e=QeTmb6
| 5.4 | Maintenance of Fire Detection System | • Fire detection and alarm system is used to identify fire at a very early stage. These systems detect the presence of smoke, heat, or flames and alert the building occupants and emergency responders, allowing for a quick and safe evacuation. Preventive maintenance is essential for the reliable and effective operation of fire detection and alarm systems. It helps ensure prevent unwanted false alarms, increase lifespan, and ultimately save lives and property. | • NFPA 72 Chapter 14
https://nirapon.sharepoint.com/:f:/s/NiraponDocumentCenterbd/ErftK0LvoRlHs7gFc-YYlNUBtvEtBkJJlpNNSMyqbc4o3Q?e=LDH0L3
| 5.5 | Fire Extinguisher Maintenance | • Preventive maintenance of fire extinguishers is essential to ensure that they are in proper working condition and can effectively operated when needed. It can help prevent avoiding malfunctions, such as leaks or clogged nozzles. Regular maintenance of fire extinguishers can be more cost-effective than repairing or replacing them after a malfunction. Additionally, a properly maintained fire extinguisher can help prevent fires from spreading, potentially reducing property damage and related costs. | • NFPA 10 Chapter 5, 6, 7 and 8
https://nirapon.sharepoint.com/:f:/s/NiraponDocumentCenterbd/EolglQoO4MBCr0ks5h_XXvUButbtiO-Sx5A5xVFPSMd5Jw?e=3LiuN2
Electrical Engineering Systems Preventative Maintenance (Includes Generator and Substation) | 6.1 | Generator, Generator room and related electrical equipment Maintenance ((e.g. Automatic Transfer Switch (ATS), Change over switch (COS) etc.) | • Generators are critical pieces of equipment for industries, providing backup power in the event of a power outage or in locations where access to the grid is limited or non-existent. • Preventative maintenance is essential for the reliable and safe operation of generators in a factory. It helps to improve efficiency, extend the lifespan of the generators. • By investing in preventative maintenance, factories can avoid costly downtime, reduce operating costs, and increase the safety of their workers. | • Generator, Generator room and related electrical equipment Maintenance format (sample) • NFPA 110 (Edition 2022),NFPA 70B (Edition 2023)
https://nirapon.sharepoint.com/:f:/s/NiraponDocumentCenterbd/EhobKwBjgFBJhrIOmqx7c10B0AGoQ1AtQKO0qm6j7xJfBA?e=aHHezh
| 6.2 | Inspection & Testing of Transformer, Substation room and related electrical equipment Maintenance | • Substations are important components of a factory's electrical infrastructure, providing voltage regulation, power distribution, protection, and reliability. They play a critical role in ensuring the safe and efficient operation of the factory's equipment, and any observations with the substation can result in lost productivity and revenue. • Preventative maintenance is essential for the reliable and safe operation of a factory's electrical power supply. It helps to improve efficiency, extend the lifespan of Transformer, Substation and related electrical equipment. • By investing in preventative maintenance, factories can avoid costly downtime, reduce operating costs, and increase the safety of their workers. | • Inspection & Testing of Transformer, Substation room and related electrical equipment maintenance format (sample) • NFPA 70B (Edition 2023) Annex E, FIGURE E.15 TRANSFORMER TEST AND INSPECTION REPORT.
https://nirapon.sharepoint.com/:f:/s/NiraponDocumentCenterbd/Evjl9hopTO9Fk9kJWWl99NUB9kXOhydEeSQaXdyGPBVM-Q?e=XG3TOe
| 6.3 | IPS, UPS (Used as backup power of machineries, emergency system etc.) Maintenance | • Maintenance of IPS/UPS is vital for ensuring that emergency backup systems are reliable, effective, and ready to use in the event of an emergency and safe operation of sophisticated machineries. | • NFPA 111 (Edition 2022) Chapter 8, Table A.8.3.2 indicates suggested Procedures, Figure A.8.4.2. • NFPA 70B (Edition 2023) FIGURE E.24 Typical Uninterruptible Power Supply System Inspection Checklist.
https://nirapon.sharepoint.com/:f:/s/NiraponDocumentCenterbd/ElfaK6OW95pHmcGbOtTTFR0B6jImEVQGAVy71o5Ji1ik2g?e=6ufPop
| 6.4 | Electrical Distribution Board Maintenance & Circuit Breaker Test | • Electrical distribution boards play a critical role in ensuring the safe and efficient operation of a factory's electrical infrastructure. They provide power distribution, circuit protection, convenience, customization, and safety. Any observations with the distribution board can result in power outages, equipment damage, and safety hazards, leading to lost productivity and revenue. • Preventative maintenance is essential for the reliable and safe operation of generators in a factory. It helps to improve efficiency, extend the lifespan of the electrical distribution board maintenance. • By investing in preventative maintenance, factories can avoid costly downtime, reduce operating costs, and increase the safety of their workers. • 80% of fires in factories are caused by electrical issues. This risk can be reduces with proper maintenance. | • NFPA 70B (Edition 2023) Annex E, FIGURE E.14 (Typical Panelboard/ Circuit Breaker Test Report). • Electrical distribution board related maintenance format (sample)
https://nirapon.sharepoint.com/:f:/s/NiraponDocumentCenterbd/Er0ecWOOblFGmc3XFGnjCVoBq9wK_ug_f2H-6AbIlK4ibg?e=hmnxWi
| 6.5 | Annual Inspection and Testing of Switchgear and protective equipment (e.g. ACB,VCB/LBS) | • Inspection and Testing of ACB, VCB/LBS, transformers, ATS/COS, and other electrical components are important for ensuring the safety, reliability, efficiency, and cost-effectiveness of a factory's electrical system. • Regular inspection and testing can help prevent accidents, equipment failures, lost production, increased energy usage, and unnecessary expenses. | • NFPA 70B (Edition 2023) Annex E • Annual Inspection and Testing of Switchgear and protective equipment
https://nirapon.sharepoint.com/:f:/s/NiraponDocumentCenterbd/EoQTxwimhctLk6pZf_yFqEwBHiJpyFmsJHJc6n-8L7NROw?e=vHZQfV
| 6.6 | Lightning Protection System Maintenance | • A lightning protection system is important for a factory to protect personnel, equipment, and property from the potential damage of a lightning strike. • Preventative maintenance of an LPS system in a factory can ensure the system's effectiveness, reduce the risk of system failure, extend the system's lifespan, and improve safety and efficiency. | • NFPA 780 (Edition 2023) Annex D Inspection and Maintenance of Lightning Protection Systems • Lightning protection system maintenance format (sample)
https://nirapon.sharepoint.com/:f:/s/NiraponDocumentCenterbd/Etr9Gf0-1l9JnAsSe6vtSq0B99upb9yX5bIeimp9Rykzww?e=dml1vy
| 6.7 | Thermographic Scan | • A preliminary approach for identifying problems in an electrical circuit is to perform a thermographic scan to check for hot points. To ensure appropriate maintenance of electrical equipment, it is advised that a thermographic scan be conducted every four months on all electrical equipment to detect any hot points. If a hot point is observed, it is crucial for the factory to perform a root cause analysis and take immediate corrective action. •The category 1 hotspots would almost certainly be category 2 or perhaps even category 3 over time if not addressed. | • ASTM E1934 & NETA MTS 2007 Tables
https://nirapon.sharepoint.com/:f:/s/NiraponDocumentCenterbd/ElU2B_pjsSlGpv9PEcwp9T4BioAT_CujUiRz87uNJgdZ7Q?e=SOdos3
| 6.8 | Insulation Resistance Measurement | • Insulation resistance measurement is essential for identifying any deterioration in the insulation of electrical conductors. It ensures that the insulation is functioning correctly and can prevent electrical hazards, such as electric shock or short circuits. By measuring the insulation resistance regularly, potential safety hazards can be identified and addressed before they become more significant complication, ensuring personnel safety and the reliability of the electrical system. | • BNBC 2006 (Existing Building), BNBC 2020 (New Building)
https://nirapon.sharepoint.com/:f:/s/NiraponDocumentCenterbd/EhJSCC-xqVhAuVR8hNDVIhoB6SOcvaNfut2xzzx18aacLQ?e=XUTaWG
| 6.9 | Earth Resistance Measurement | • Earth resistance measurement ensures the safety of electrical systems and personnel. It measures the effectiveness of the earth electrode, preventing electric shock or equipment damage. Regular measurement can identify potential issues, ensuring safety and efficiency, and minimizing the risk of injury or damage. | • BNBC 2006 (Existing Building), BNBC 2020 (New Building)
https://nirapon.sharepoint.com/:f:/s/NiraponDocumentCenterbd/En1ucKVnwXhJuXPt0yYpQ6IBHOcn7w_1yYn9kKANI5GkNQ?e=oOHfSB
| 6.1 | Transformer Oil Test | • Testing the dielectric properties of transformer oil is crucial for ensuring the safety and performance of oil-type transformers. • Proper oil quality through regular testing ensures safe and efficient operation, reducing downtime and safety hazards. | • NETA MTS 2007 Tables
https://nirapon.sharepoint.com/:f:/s/NiraponDocumentCenterbd/Enc2hfep2VpEh3KEANtCdnUBqBtwFCfMcs4hVeYcffjDkw?e=E6MaBd
| 6.11 | Solar System Maintenance | • The overarching goal of preventative maintenance is to ensure maximum yield, system uptime, and efficiency of a solar array. • By maintaining the system on a regular basis, it stays in better working condition, and ensures potential malfunctions are effectively managed. | • NFPA 70B (Edition 2023) Chapter 30
https://nirapon.sharepoint.com/:f:/s/NiraponDocumentCenterbd/EoLSy9yRrzNAmAfHyMhuXX8BgXzPYq0qyKvzwTevpSgGYQ?e=PZpw9u
| 6.12 | Electrical Load Management Program | • Electrical load management is essential for preventing equipment failure, safety hazards, and downtime. Appropriate load distribution increases efficiency, reduces energy waste and costs, and identifies potential issues before they cause problems. Effective load management ensures a safe and reliable power supply for factory operations | • BNBC 2006 (Existing Building), BNBC 2020 (New Building)
https://nirapon.sharepoint.com/:f:/s/NiraponDocumentCenterbd/EgU4GlVfSqhBr6gHmj4DtCEBWMNvFlK4OkdAQ8SvUne8JQ?e=YJWY61
| 6.13 | General Electrical System Maintenance (e.g., BBT, Light fixtures with cover in storage area etc.) and other electrical equipments (e.g., Machine, Lift, AC etc.) | • About 80% fire incident occurs due to electrical faults in factory. Overlooking preventative maintenance of an electrical system can result in equipment failure, safety hazards, reduced efficiency, increased repair costs all of which can be costly and disruptive to a factory. • It is important to prioritize regular maintenance of electrical systems to ensure their safe and efficient operation. | • BNBC 2006 (Existing Building), BNBC 2020 (New Building)
https://nirapon.sharepoint.com/:f:/s/NiraponDocumentCenterbd/EnwrGXTi2AJHpChRkBPHHbsB1MSjr_PMkUrthj6kxDIojg?e=2aLDIC
Structural Load Management and Preventative Maintenance Programme | 7.1 | Factory Floor Load Management program | • A floor load management policy is a set of guidelines and procedures that govern how loads are managed on the factory floor. This policy also helps to make contingency plan for load management (if delay shipment of goods). Effective logistics & production planning improve floor load management planning. • A floor load management program helps ensure that the weight and distribution of loads on the factory floor are within safe limits. This prevents damage to the building's structure and reducing the risk of collapse due to overloaded or unbalanced loads. • A floor load management program ensures that loads are properly distributed and managed in a floor. It is also minimize additional fire safety challenges. | https://nirapon.sharepoint.com/:f:/s/NiraponDocumentCenterbd/EiPFP7IuUY1Euv6fkqxceeMBsALpYTEym2AVzJfXBO4nRA?e=qXcfV3
| 7.2 | Dampness and Water Ponding Maintenance | • Dampness on structural member can weaken the structure of a building and lead to decay and even collapse. Regular maintenance can help prevent these issues and ensure the structural integrity of the building. • Dampness and water ponding can create a breeding ground for mold, mildew & harmful microorganisms that can cause health problems such as allergies and respiratory illnesses. Regular maintenance can help prevent these issues. • If water stands long duration on the roof & floor, structural cracks will appear on the roof & floor due to rebar corrosion of the slab. Water ponding can lead to water damage to roof & floors, which can be costly to repair. • Regular periodic maintenance can help prevent water damage and extend the lifespan of building components. • Regular maintenance can help prevent costly repairs & replacements by identifying & addressing issues early. | https://nirapon.sharepoint.com/:f:/s/NiraponDocumentCenterbd/EixU912m8XxLtMst3h8EMZ8BBFb2u2oaT7_2CMTiI8PzBg?e=fKOyMV
| 7.3 | Corrosion Maintenance | • Corrosion maintenance is particularly important for steel buildings since steel is highly susceptible to corrosion. • Corrosion can weaken steel beams, columns, and other structural components of the building, leading to potential collapse or failure. Regular maintenance can help identify and address corrosion issues before they compromise the safety of the building. • Regular periodic maintenance can help prevent corrosion damage and extend the lifespan of steel components of building. | https://nirapon.sharepoint.com/:f:/s/NiraponDocumentCenterbd/EiF5wNWKwx9Ct8n6cn2-ESUBETU1FXr6iv-LaI_sEfmiRg?e=ecNfer
| 7.4 | Structural Crack Maintenance | • Structural Members of the Building are the components which take (and resist) the load. As example: Foundation, Column, Beam, Slab etc. are Structural Member of Building. If cracks appear in Building skeleton(Column, Beam, Slab, Beam-Column Joint, Grade Beam, Foundation etc.), then it is a structural crack. • Regular checking of structural cracks in a building is important for identifying and addressing potential issues before they become significant problems. • Structural cracks can be an indication of underlying issues with the building's foundation, column, beam or other structural elements that, if left unaddressed long time, can lead to significant damage or collapse. • By identifying and addressing these issues early on, repair cost can be minimized. | https://nirapon.sharepoint.com/:f:/s/NiraponDocumentCenterbd/EnASZTnT1DRGvI_3xaklN6gBV8CLLJM8N77jeqAKa5L1NQ?e=1eTtUf
| 7.5 | Non-Structural Crack Maintenance | • Non-structural Members of the Building are the components which don't take (and resist) the load. As example: Non load bearing brick wall, partition wall & brick wall joint etc. are Non-structural Member of Building. • Regular checking of non-structural cracks can help detect issues early on, before they become more significant problems. Early detection can help prevent costly repairs and replacements and extend the lifespan of building components. • Sometimes, Non-structural crack may appear on Non-structural element due to structural inadequacy (e.g. Soil Settlement). If it is unaddressed in early stages, then this become significant problems. • Non-structural cracks can allow water to enter the building, leading to water damage, mold growth, and other issues. Regular checking of non-structural cracks can help identify and repair these cracks, preventing costly water damage and other problems. | https://nirapon.sharepoint.com/:f:/s/NiraponDocumentCenterbd/EspsTU2Kq6pDknaS7n6mB_sBo89UwM_qfnEStX03LPDRnA?e=uGnwdU
| 7.6 | Non-Structural Element Anchorage and Structural Bracing Maintenance | • Anchoring & bracing check of Non-structural element (storage racks, water tank, steam pipe etc.) should be covered under this checklist for all buildings. Bracing check of structural element (cable bracing at roof & wall if present) should also be covered under this checklist for all buildings. • Non-structural elements such as storage racks, PVC water tanks, HVAC systems, and piping can become displaced and even fall during an earthquake. Anchoring these elements can prevent them from falling and causing injury or damage to people and property. Non-structural element anchorage can improve the overall performance of a building during a seismic event. • Structural bracing is an important component of the building's structural system that helps distribute loads and resist lateral forces, such as wind or earthquake forces. Regular checking of the bracing can identify any damage or deterioration that could compromise the building's structural integrity, which could lead to collapse or other safety hazards. Early identification of issues can prevent further damage and ensure that the building's structural integrity is maintained. Regular maintenance of structural bracing can improve the overall performance of the building during a seismic event. | https://nirapon.sharepoint.com/:f:/s/NiraponDocumentCenterbd/Er1QH1yv6IBHlihPURBUCVUBpB8aWpdZkGLARqDiRzBRlQ?e=sEEgya
Maintenance of other utilities - Boilers, Compressors HVAC systems, Compressed Gas cylinders and Gas Connection and Emergency Light and Exit Sign | 8.1 | Emergency Light and Exit Sign Maintenance | • In an emergency, occupants may need to find an exit to evacuate. In the case of a power outage, visible exit signs and backup emergency lighting can guide people throughout the facility to find the exit and evacuate safely. • Lack of maintenance can cause non-functionality, less illumination, insufficient battery back up of emergency light and exit sign. Exit signs without visibility and emergency light without sufficient illumination could not help the occupant to find an exit and evacuate safely. Functionality, illumination level, battery backup of emergency light and exit signage should be checked periodically. | • NFPA 101 Edition 2018 Section 7.9.3, Section 7.10.9
https://nirapon.sharepoint.com/:f:/s/NiraponDocumentCenterbd/EqW5gvbrc8FPvSjRfqSlul0B4Czp4tJ-thY36UWcaB6SXA?e=eQVq10
| 8.2 | Compressed Gas Cylinder and Gas Connection Maintenance | • Compressed gas cylinders can be extremely hazardous when misused or not maintained. Without proper use and care compressed gas cylinders can explode killing workers and destroying equipment. Also, improper handling of cylinders could result in sprains, strains, falls, bruises, and broken bones. Chemical burns, poisoning, and cold burns could occur if gases accidentally escape from the cylinder due to mishandling • Poorly maintained gas connection can cause failure of the line. A leak in the connection is unsafe because natural gas is flammable and dangerous when not contained. Leaking gas can cause a fire or other types of property damage, so gas line maintenance is essential. • Careful procedures are necessary for handling the various compressed gases, cylinders, regulators or valves used to control gas flow, and the piping used to confine gases during flow. | • OSHA Compressed Gases Standard (Section 1910.101)
https://nirapon.sharepoint.com/:f:/s/NiraponDocumentCenterbd/Ev17HBF4CrVIrzWdWC_ypWEBko3hn1nlJpL4m5hjE4adOA?e=f6kSXp
| 8.3 | Boiler & Compressor Maintenance | • Boilers that are not properly maintained can cause hazardous conditions and increase the risk of fire, gas leaks, and explosions. Also, it reduces the efficiency, increase the fuel costs etc. • A poorly maintained compressor may be generating excessive heat and noise, and unseen or unidentified issues can lead to things like fire hazards, electrical shorts; it can even indirectly cause other machines to malfunction. • A regular preventative maintenance helps to ensure cost savings, decreased equipment downtime, improved safety & reliability, and un-interruption in operation. | https://nirapon.sharepoint.com/:f:/s/NiraponDocumentCenterbd/EoCAgj6PdsBFoH6zjW9yrrYBKStcRVgSFIyKu2m45iSMMg?e=itkNAp
| 8.4 | HVAC Maintenance | • Lack of maintenance of HVAC system can cause accumulation of dust, fault in electrical wiring, failure of system components, leakage in ducts, fault in installed fire dampers etc. which can lead an HVAC system as a dangerous fire hazard. Also, poorly maintained ducts can draw carbon monoxide, bacteria, viruses, allergens, mold and other unhealthy substances into the air which can create health problem in the long run for the users. | https://nirapon.sharepoint.com/:f:/s/NiraponDocumentCenterbd/EpqDe28TPTtPmr0ZIs_AzFsBZ8hB5vZYNNBn3OMJHQqXPw?e=qyo1Ia

## Technical Changes & Updates
Factory Name |  |  | FFC ID
Factory Address |  |  | Number of People**
** If multiple business ID (FFC ID) located in same locale then number of people should be provided as per business ID
Complete only for Technical Changes & Updates (As Applicable) Please refer to Guidance Note at the start of this report
Details |  | Comments from Factory | Response from Factory
Yes / No / Not Applicable
9 | Structural changes - please identify any changes such as extension, expansion, new buildings or other layout changes that might impact the structural integrity of any buildings. (briefly define extension, expansion and new building)?
Electrical changes - has there been any changes to the electrical system such as an increased power requirement, or changes in the use of any room or any extension, expansion or new building?
Fire safety and engineering changes - has there been any changes in the use of rooms, changes within the original fire separation solution, fire detection and protection systems. Has there been any extension, expansion or new building added?
An extension is defined as a vertical or horizontal addition of a new structure to the building. This extended structure will be structurally linked to the original CAP closed factory. The extended structure will also have shared utilities and engineered safety solutions for example, the same utilities supply, hydrant system and CFDS as the original building. This extension can be vertical (additional stories) or horizontal (a structure is laterally attached to a building elevation. An expansion is defined as a building that is additional to the CAP closed building. This building is structurally independent of the original CAP closed building. However, the factory will be linked by utilities and some or all engineered safety solutions. For example, hydrant system, central fire detection system, electrical supply etc.
If uncertain then please describe any areas of concern in which it is possible that changes have been made and Nirapon will provide advice and guidance on next steps.

## Contact Updates
Fill this section only if any contact is updated
Contact Updates | Feedback from Factory
Factory Name:
Factory Address:
General Manager Name:
General Manager Email address:
General Manager Phone Number:
Factory Manager Name:
Factory Manager Email address:
Factory manager Phone number:
Welfare/Counselor Director or Manager Name:
Welfare/Counselor Director or Manager Email address:
Welfare/Counselor Director or Manager Phone number:
Compliance Manager Name:
Compliance Manager Email address:
Compliance Manager Direct Phone Number:
Key Contact Person for Safety Related Communication-Name:
Key Contact Person for Safety Related Communication-Email:
Key Contact Person for Safety Related Communication-Direct Phone Number: